## Sheet1
CHARGING
Variable | Description | Source / equation | Constraints
PBapp | Will be set to a negative value in the software | Addon config setting | PBapp <= 0
PBnow | Can be negative (charging the battery) or positive (discharging). Negative value most likely as we want to be charging | Read from battery inverter modbus
PGnow | Can be negative (drawing power from grid) or positive (supplying to grid). Negative value most likely as we are charging | Read from data manager (energy meter) modbus
VGnow | Measured voltage at grid connection point. Always a positive value | Read from data manager (energy meter) modbus | 0 < VGnow
Imax | Main fuse current limit at grid connection point. Always a positive value | Addon config setting | 0 < Imax
PGmax | Upper limit for power value when power is supplied to the grid (to protect main fuse) | PGmax = VGnow * Imax | 0 < PGmax
PGmin | Lower limit for power value when power is drawn from the grid (to protect main fuse) | PGmin = -1 * PGmax | PGmin < 0
Pother | Power consumed (negative value) or supplied (positive) elsewhere in the system (eg. heat pump or PV) | Pother = PGnow - PBnow
PBlim_min | Lower limit for battery inverter power value when charging or discharging the battery. | PBlim_min = PGmin - Pother | PBlim_min < PBlim_max
PBlim_max | Upper limit for battery inverter power value when charging or discharging the battery. | PBlim_max = PGmax - Pother | PBlim_min < PBlim_max
PBsent | Will be the max of PBapp and PBlim_min. Can be set to positive (discharging) when Pother < Pgmin | PBsent = max(PBapp, PBlim_min) | PBapp <= PBsent; PBlim_min <= Pbsent
NOTE: there might be a scenario where Pother is very negative (a lot of consumption by car charging and heat pump) and lower than PGmin. In that case PBlim_min becomes positive, indicating that the battery should actually discharge to protect the main fuse.
DISCHARGING
Variable | Description | Source / equation | Constraints
PBapp | Will be set to a positive value in the software | Addon config setting | 0 <= PBapp
PBnow | Can be negative (charging the battery) or positive (discharging). Positive value most likely as we want to be discharging | Read from battery inverter modbus
PGnow | Can be negative (drawing power from grid) or positive (supplying to grid). Positive value most likely as we are discharging | Read from data manager (energy meter) modbus
VGnow | Measured voltage at grid connection point. Always a positive value | Read from data manager (energy meter) modbus | 0 < VGnow
Imax | Main fuse current limit at grid connection point. Always a positive value | Addon config setting | 0 < Imax
PGmax | Upper limit for power value when power is supplied to the grid (to protect main fuse) | PGmax = VGnow * Imax | PGmin < 0 < PGmax
PGmin | Lower limit for power value when power is drawn from the grid (to protect main fuse) | PGmin = -1 * PGmax | PGmin < 0 < PGmax
Pother | Power consumed (negative value) or supplied (positive) elsewhere in the system (eg. heat pump or PV) | Pother = PGnow - PBnow
PBlim_min | Lower limit for battery inverter power value when charging or discharging the battery. | PBlim_min = PGmin - Pother | PBlim_min < PBlim_max
PBlim_max | Upper limit for battery inverter power value when charging or discharging the battery. | PBlim_max = PGmax - Pother | PBlim_min < PBlim_max
PBsent | Will be the min of PBapp and PBlim_max. Can be set to negative (charging) when Pother > Pgmax | PBsent = min(PBapp, PBlim_max) | PBsent <= PBapp; PBsent <= PBlim_max
NOTE: there might be a scenario where Pother is very positive (a lot of PV production) and greater than PGmax. In that case PBlim_max becomes negative, indicating that the battery should actually charge to protect the main fuse.