## Sheet1
Mode 4 Algorithm
Likelihood
Mode 4 objective: determine optimal charging/limiting schedule to maximize revenu |  |  |  |  | COMMON
UNCOMMON
During each control loop cycle, the desired power levels from the schedule are applied for each controlled device, followed by a: |  |  |  |  | RARE
Check layer: avoid unnecessary costs (eg. Execessive solar generation during periods of negative prices) |  |  |  |  | IMPOSSIBLE
Safety layer: ensure power levels remain within grid connection limits
|  |  | Negative power at grid connection (power drawn from grid) |  | Positive power at grid connection (power supplied to grid)
PRICES | Solar power generation | Amount of control | Close to PGmin | Not close to PGmin | Close to PGmax | Not close to PGmax
Positive Prices | Significant solar power generation | Full - all configured devices being controlled | Max battery charging and/or positive Pother using (costly) power from the grid. Solar power alone apparently not sufficient to satisfy demand. Batteries being charged to benefit from higher prices later. ACTION: limit battery inverters to stay below limit | Some solar power, but not enough to fully cover demand (battery charging and/or Pother), so additional charging from grid necessary. NO ACTION | Max battery discharging and/or high solar power generation. Supplying to the grid at PGmax limit could be desirable to maximize profit. ACTION: limit battery discharge first (iff discharging), then solar power to stay close to PGmax | Battery discharging and/or solar power generation during a period of positive prices. NO ACTION
|  | Degraded - one or more configured devices (temporarily) uncontrolled | Most likely one or more uncontrolled battery inverters is doing max charging, possibly combined with some Pother. ACTION: send HA message and limit charging of other controlled inverters on the same phase, if possible | Most likely one or more uncontrolled battery inverters is charging. Solar power is alleviating the situation, but could still be dangerous if power levels are not far from PGmin once solar power is reduced. ACTION: send HA message and limit charging, if possible | Either uncontrolled, discharging battery inverter or uncontrolled solar inverter. ACTION: send HA message and limit battery discharging and/or lower solar set point, if possible | Either discharging uncontrolled battery inverter or uncontrolled solar inverter. Could be dangerous if power levels are not far from PGmax. ACTION: send HA message and limit battery discharging and lower solar set point, if possible
| Insignificant solar power generation | Full - all configured devices being controlled | Max battery charging and/or positive Pother using (costly) power from the grid. Batteries being charged to benefit from higher prices later. ACTION: limit battery charging to stay below limit | Some battery charging and/or Pother. NO ACTION | Max battery discharging. Supplying to the grid at PGmax limit could be desirable to maximize profit. ACTION: limit battery discharge to stay below limit | Battery discharging during a period of positive prices. NO ACTION
|  | Degraded - one or more configured devices (temporarily) uncontrolled | Most likely one or more uncontrolled battery inverters is doing max charging, possibly combined with some Pother. ACTION: send HA message and limit charging of other controlled inverters on the same phase, if possible | Most likely one or more uncontrolled battery inverters is charging. Could be dangerous if power levels are not far from PGmin. ACTION: send HA message and limit charging of other inverters on the same phase, if possible | Uncontrolled, discharging battery inverter. ACTION: send HA message and limit battery discharging of inverters on the same phase, if possible | Discharging uncontrolled battery inverter. Could be dangerous if power levels are not far from PGmax. ACTION: send HA message and limit battery discharging, if possible
Negative Prices | Significant solar power generation | Full - all configured devices being controlled | Max battery charging and/or positive Pother using power from the grid. Being paid to consume power, so desirable to stay close to this limit. ACTION: limit solar inverters first, then limit battery inverters to stay close to this limit | Net power drawn from grid, battery charging and Pother exceeds solar power. ACTION: limit solar inverter to increase net power drawn from grid and maximize profit | Most likely high solar power generation or some battery discharging. Supplying to the grid at PGmax limit is highly undesirable. Unlikely that the schedule warrants battery discharging ACTION: limit solar power to net PGmin | Most likely high solar power generation or some battery discharging. Supplying to the grid with negative prices is highly undesirable. Unlikely that the schedule warrants battery discharging ACTION: limit solar power to net PGmin
|  | Degraded - one or more configured devices (temporarily) uncontrolled | Most likely one or more uncontrolled battery inverters is doing max charging, possibly combined with some Pother. ACTION: send HA message and limit charging of other controlled inverters on the same phase, if possible | Most likely one or more uncontrolled battery inverters is charging. Solar power is alleviating the situation, but could still be dangerous if power levels are not far from PGmin once solar power is reduced. ACTION: send HA message and limit charging, if possible | Either uncontrolled, discharging battery inverter or uncontrolled solar inverter. ACTION: send HA message and limit battery discharging and/or lower solar set point, if possible | Either discharging uncontrolled battery inverter or uncontrolled solar inverter. Could be dangerous if power levels are not far from PGmax. ACTION: send HA message and limit battery discharging and lower solar set point, if possible
| Insignificant solar power generation | Full - all configured devices being controlled | Max battery charging and/or positive Pother using power from the grid. Being paid to consume power, so desirable to stay close to this limit. ACTION: limit battery inverters to stay close to this limit | Power drawn from grid for battery charging and Pother. NO ACTION | Must be battery discharging. Supplying to the grid at PGmax limit is highly undesirable. Unlikely that the schedule warrants battery discharging now and at this power level. ACTION: send HA message and limit battery discharging | Must be battery discharging. Supplying to the grid is undesirable, but could be possible to create battery capacity to profit from even lower prices later. NO ACTION
|  | Degraded - one or more configured devices (temporarily) uncontrolled | Most likely one or more uncontrolled battery inverters is doing max charging, possibly combined with some Pother. ACTION: send HA message and limit charging of other controlled inverters on the same phase, if possible | Most likely one or more uncontrolled battery inverters is charging. Could be dangerous if power levels are not far from PGmin. ACTION: send HA message and limit charging of other inverters on the same phase, if possible | Uncontrolled, discharging battery inverter. ACTION: send HA message and limit battery discharging of inverters on the same phase, if possible | Discharging uncontrolled battery inverter. Could be dangerous if power levels are not far from PGmax. ACTION: send HA message and limit battery discharging, if possible